## Slide 1: Trip Curves
LT tested at 3x CT rating or LT setting
Follow top and bottom of band to determine acceptable trip time band
Draw line down from the 3x scale
Should trip at 40-60 seconds @ 300%